## Leyenda
Listado de modelos dinámicos admitidos por el operador del sistema
Índice
Hoja 1 | Generadores, motores y cargas
Hoja 2 | Compensadores de tensión
Hoja 3 | Sistemas de excitación
Hoja 4 | Estabilizadores de potencia (PSS)
Hoja 5 | Limitadores de mínima excitación (UEL)
Hoja 6 | Limitadores de máxima excitación (OEL)
Hoja 7 | Controlador de carga de la turbina
Hoja 8 | Reguladores de velocidad-turbina (governors)
Hoja 9 | Generación eólica
Hoja 10 | SVC, FACTS, shunts
Hoja 11 | Protecciones de tensión y frecuencia (mínima y máxima)
Hoja 12 | REFERENCIAS
Los modelos de aceptados por el operador del sistema son únicamente los que figuran en la columna "Modelo PSS/E"
Referencia:
2020-12-01
DF.20_101

## Gen., mot. y cargas
1) Generadores, motores y cargas
Denominación | IEEE standard1 | Modelo CIM | Modelo PSS/E | Revisión 2021
EPRI battery energy storage FACTS model |  |  | CBEST | SI
American Superconductor DSMES (Distributed Superconducting Magnetic Energy Storage device model) |  |  | CDSMS1 | SI
Third order generator model |  |  | CGEN1 | NO
Induction generator model with rotor flux transients |  | GenAsync | CIMTR1 | SI
Induction motor model with rotor flux transients |  | MotorAsync | CIMTR2 | SI
Induction generator model with rotor flux transients |  | GenAsync | CIMTR3 | SI
Induction motor model with rotor flux transients |  | MotorAsync | CIMTR4 | SI
EPRI superconducting electromagnetic energy storage FACTS model |  |  | CSMEST | SI
Static condenser FACTS model |  |  | CSTATT | SI
SCR controlled static var source model |  |  | CSVGN1 | SI
SCR controlled static var source model |  |  | CSVGN3 | SI
SCR controlled static var source model |  |  | CSVGN4 | SI
WECC controlled static var source model |  |  | CSVGN5 | SI
WECC controlled static var source model |  |  | CSVGN6 | SI
Salient pole frequency changer model |  |  | FRECHG | NO
Classical generator model |  | GenEquiv | GENCLS | NO
Round rotor generator model with dc offset torque component |  |  | GENDCO | SI
Round rotor generator model |  |  | GENROE | SI
Round rotor generator model (modelo de generador de rotor liso) |  | RoundRotor / GenSync | GENROU | SI
Salient pole generator model |  |  | GENSAE | SI
Salient pole generator model (modelo de generador de polos salientes) |  | SalientPole / GenSync | GENSAL | SI
Transient level generator model (modelo de generador para transitorios) |  | Transient | GENTRA | NO
WECC Type J Synchronous generator model |  |  | GENTPJU1 | SI
Model to Play-In known voltage and/or frequency signal |  |  | PLBVFU1 | NO
User written performance based model of single phase air conditioner motor. |  |  | ACMTxxU1 | SI
Induction motor model |  | LoadMotor | CIM5xx | SI
Induction motor model |  |  | CIM6xx | SI
Induction motor model (WECC) |  | LoadMotor | CIMWxx | SI
Complex load model |  |  | CLODxx | SI
Composite load model |  |  | CMLDxxU1 | SI
Composite load model (revised versions of CMLDxxU1) |  |  | CMLDxxU2 | SI
Extended-term load reset model |  |  | EXTLxx | SI
IEEE load model |  | Exponential,ZIP1* | IEELxx | SI
Load frequency model |  | ZIP2* | LDFRxx | SI
(1) IEEE Std 1110-1991IEEE Guide for Synchronous Generator Modeling Practices in Stability Analyses
Recomendado
(*)
Note on E30: Soto Cano, Lourdes: ACMTBLU1, ACMTOWU1, ACMTZNU1, ACMTARU1, ACMTALU1
Note on E31: Sergio Martínez: CIM5BL, CIM5OW, CIM5ZN, CIM5AR, CIM5AL
Note on E32: Sergio Martínez: CIM6BL, CIM6OW, CIM6ZN, CIM6AR, CIM6AL
Note on E33: Sergio Martínez: CIMWBL, CIMWOW, CIMWZN, CIMWAR, CIMWAL
Note on E35: Sergio Martínez: CLODBL, CLODOW, CLODZN, CLODAR, CLODAL
Note on E36: Soto Cano, Lourdes: CMLDBLu1, CMLDOWU1, CMLDZNU1, CMLDARU1, CMLDALU1
Note on E37: Soto Cano, Lourdes: CMLDBLU2, CMLDOWU2, CMLDZNU2, CMLDARU2, CMLDALU2
Note on E38: Sergio Martínez: EXTLBL, EXTLOW, EXTLZN, EXTLAR, EXTLAL
Note on E39: Sergio Martínez: IEELBL, IEELOW, IEELZN, IEELAR, IEELAL
Note on E40: Sergio Martínez: LDFRBL, LDFROW, LDFRZN, LDFRAR, LDFRAL

## Comp. tensión
2) Compensadores de tensión
Denominación | IEEE standard | Modelo CIM | Modelo PSS/E
Voltage regulator compensating model | IEEE Voltage Compensation Model | VcompIEEE | COMP
Cross compound compensating model |  | VcompCROSS | COMPCC
1981 IEEE voltage compensating model | IEEE Voltage Compensation Model | VcompIEEE | IEEEVC
Remote bus voltage signal model |  |  | REMCMP
Cross-Current Compensation model with Reactive Current Feedback |  |  | CCOMP4U1
Recomendado

## S.Excit
3) Sistemas de excitación
Denominación | IEEE standard 1 | Modelo CIM | Modelo PSS/E
IEEE 421.5 2005 AC7B excitation system | IEEE (2005) AC7B Model | ExcAC7B | AC7B
IEEE 421.5 2005 AC8B excitation system | IEEE (2005) AC8B Model | ExcAC8B | AC8B
Brown-Boveri static excitation system model |  |  | BBSEX1
Czech proportional/integral excitation system model |  |  | BUDCZT
ELIN brushless excitation system model |  |  | CELIN
IEEE 421.5 2005 DC3A excitation system | IEEE (1992/2005) DC3A Model |  | DC3A
IEEE 421.5 2005 DC4B excitation system | IEEE (2005) DC4B Model | ExcDC4B | DC4B
AEP Rockport excitation system model |  |  | EMAC1T
1992 IEEE type AC1A excitation system model | IEEE (1992/2005) AC1A Model | ExcAC1A | ESAC1A
1992 IEEE type AC2A excitation system model | IEEE (1992/2005) AC2A Model | ExcAC2A | ESAC2A
1992 IEEE type AC3A excitation system model | IEEE (1992/2005) AC3A Model | ExcAC3A | ESAC3A
1992 IEEE type AC4A excitation system model | IEEE (1992/2005) AC4A Model | ExcAC4A | ESAC4A
1992 IEEE type AC5A excitation system model | IEEE (1992/2005) AC5A Model | ExcAC5A | ESAC5A
1992 IEEE type AC6A excitation system model | IEEE (1992/2005) AC6A Model | ExcAC6A | ESAC6A
Basler DECS model | IEEE (2005) AC8B Model | ExcAC8B | ESAC8B
1992 IEEE type DC1A excitation system model | IEEE (1992/2005) DC1A Model | ExcDC1A | ESDC1A
1992 IEEE type DC2A excitation system model | IEEE (1992/2005) DC2A Model | ExcDC2A | ESDC2A
1992 IEEE type ST1A excitation system model | IEEE (1992/2005) ST1A Model | ExcST1A | ESST1A
1992 IEEE type ST2A excitation system model | IEEE (1992/2005) ST2A Model | ExcST2A | ESST2A
1992 IEEE type ST3A excitation system model | IEEE (1992/2005) ST3A Model | ExcST3A | ESST3A
IEEE type ST4B potential or compounded source-controlled rectifier exciter | IEEE (2005) ST4B Model | ExcST4B | ESST4B
Modified IEEE Type AC1A excitation |  |  | ESURRY
EX2000 Excitation System |  |  | EX2000
1981 IEEE type AC1 excitation system model | IEEE (1992/2005) AC1A Model | ExcAC1A | EXAC1
A Modified type AC1 excitation system model | IEEE (1992/2005) AC1A Model | ExcAC1A | EXAC1A
1981 IEEE type AC2 excitation system model | IEEE (1992/2005) AC2A Model | ExcAC2A | EXAC2
1981 IEEE type AC3 excitation system model | IEEE (1992/2005) AC3A Model | ExcAC3A | EXAC3
1981 IEEE type AC4 excitation system model | IEEE (1992/2005) AC4A Model | ExcAC4A | EXAC4
Basler static voltage regulator feeding dc or ac rotating exciter model |  |  | EXBAS
1981 IEEE type DC2 excitation system model | IEEE (1992/2005) DC2A Model | ExcDC2A | EXDC2
Static PI transformer fed excitation system model |  |  | EXELI
Bus or solid fed SCR bridge excitation system model type NEBB (NVE) |  |  | EXNEBB
Bus or solid fed SCR bridge excitation system model type NI (NVE) |  |  | EXNI
Proportional/integral excitation system model |  |  | EXPIC1
1981 IEEE type ST1 excitation system model | IEEE (1992/2005) ST1A Model | ExcST1A | EXST1
1981 IEEE type ST2 excitation system model | IEEE (1992/2005) ST2A | ExcST2A | EXST2
Modified 1981 IEEE type ST2 excitation system model | IEEE (1992/2005) ST2A | ExcST2A | EXST2A
1981 IEEE type ST3 excitation system model |  |  | EXST3
1968 IEEE type 1 excitation system model | IEEE (1992/2005) DC1A Model | ExcDC1A | IEEET1
1968 IEEE type 2 excitation system model | IEEE (1992/2005) AC5A Model | ExcAC5A | IEEET2
1968 IEEE type 3 excitation system model | IEEE (1992/2005) ST2A Model | ExcST2A | IEEET3
1968 IEEE type 4 excitation system model |  |  | IEEET4
Modified 1968 IEEE type 4 excitation system model |  |  | IEEET5
1979 IEEE type 1 excitation system model and 1981 IEEE | IEEE (1992/2005) DC1A Model | ExcDC1A | IEEEX1
1979 IEEE type 2 excitation system model | IEEE (1992/2005) AC5A Model | ExcAC5A | IEEEX2
1979 IEEE type 3 excitation system model | IEEE (1992/2005) ST2A Model | ExcST2A | IEEEX3
1979 IEEE type 4 excitation system, 1981 IEEE type DC3 and 1992 IEEE type DC3A models | IEEE (1992/2005) DC3A Model | ExcDC3A | IEEEX4
Modified 1968 IEEE type 1 excitation system model | IEEE (1992/2005) AC1A Model | ExcAC1A | IEET1A
Modified 1968 IEEE type 1 excitation system model |  |  | IEET1B
Modified 1968 IEEE type 4 excitation system model |  |  | IEET5A
1979 IEEE type 2A excitation system model | IEEE (1992/2005) AC1A Model | ExcAC1A | IEEX2A
IVO excitation system model |  |  | IVOEX
Ontario Hydro IEEE Type ST1 excitation system with continuous and bang bang terminal voltage limiter |  |  | OEX12T
Ontario Hydro IEEE Type ST1 excitation system with semicontinuous and acting terminal voltage limiter |  |  | OEX3T
General purpose rotating excitation system model |  |  | REXSYS
General purpose rotating excitation system model |  |  | REXSY1
Bus or solid fed SCR bridge excitation system model |  | ExcSCRX | SCRX
Simplified excitation system model |  | ExcSEXS | SEXS
IEEE 421.5 2005 ST5B excitation system | IEEE (2005) ST5B Model | ExcST5B | ST5B
IEEE 421.5 2005 ST6B excitation system | IEEE (2005) ST6B Model | ExcST6B | ST6B
IEEE 421.5 2005 ST7B excitation system | IEEE (2005) ST7B Model | ExcST7B | ST7B
T High dam excitation system model |  |  | URHID
T IEEE proposed type ST5B excitation system |  |  | URST5
Modified ESAC6A Model |  |  | USAC6AU
1. La mayor parte de los modelos de sistemas de excitación están basados en el estándar de IEEE 421.5 “IEEE Recommended Practice for Excitation System Modeling for Power System Stability Studies” de 2005. También se puede hacer referencia a anteriores versiones de este estándar: 1992, 1980, y 1968. Casi todos los modelos descritos en las versiones anteriores pueden ser representados adecuadamente por modelos del estándar de 2005.
Recomendado

## Estabilizador
4) Estabilizadores de potencia (PSS)
Denominación | IEEE standard 1 | Modelo CIM | Modelo PSS/E
Transient excitation boosting stabilizer model |  |  | BEPSST
Dual-input signal power system stabilizer model |  |  | IEE2ST
1981 IEEE power system stabilizer model |  |  | IEEEST
IVO stabilizer model |  |  | IVOST
Ontario Hydro delta-omega power system stabilizer |  |  | OSTB2T
Ontario Hydro delta-omega power system stabilizer |  |  | OSTB5T
IEEE Std. 421.5-2005 PSS1A Single-Input Stabilizer model |  |  | PSS1A
1992 IEEE type PSS2A dual-input signal stabilizer model | IEEE (2005) PSS2B Model | PssIEEE2B | PSS2A
IEEE 421.5 2005 PSS2B IEEE dual-input stabilizer model | IEEE (2005) PSS2B Model | PssIEEE2B | PSS2B
IEEE Std. 421.5 2005 PSS3B IEEE dual-input stabilizer model |  |  | PSS3B
IEEE 421.5(2005) dual-input stabilizer model |  |  | PSS4B
PTI microprocessor-based stabilizer model |  |  | PTIST1
PTI microprocessor-based stabilizer model |  |  | PTIST3
Dual-input signal power system stabilizer model |  |  | ST2CUT
Speed sensitive stabilizer model |  |  | STAB1
ASEA power sensitive stabilizer model |  |  | STAB2A
Power sensitive stabilizer model |  |  | STAB3
Power sensitive stabilizer model |  |  | STAB4
Power sensitive stabilizer model type NI (NVE) |  |  | STABNI
WECC supplementary signal for static var system |  |  | STBSVC
Synchronous Condenser Auxiliary Control Model |  |  | SYNAXBU1
1. La mayor parte de los modelos de estabilzadores están basados en el estándar de IEEE 421.5 “IEEE Recommended Practice for Excitation System Modeling for Power System Stability Studies” de 2005. También se puede hacer referencia a anteriores versiones de este estándar: 1992, 1980, y 1968. Casi todos los modelos descritos en las versiones anteriores pueden ser representados adecuadamente por modelos del estándar de 2005.
Recomendado

## MinExc
5) Limitadores de mínima excitación (UEL)
Denominación | IEEE standard | Modelo CIM | Modelo PSS/E
Minimum excitation limiter model |  |  | MNLEX1
Minimum excitation limiter model |  |  | MNLEX2
Minimum excitation limiter model |  |  | MNLEX3
IEEE 421.5 2005 UEL1 under-excitation limiter |  |  | UEL1
IEEE 421.5 2005 UEL2 minimum excitation limiter |  |  | UEL2

## MaxExc
6) Limitadores de máxima excitación (OEL)
Denominación | IEEE standard | Modelo CIM | Modelo PSS/E
Maximum excitation limiter model |  |  | MAXEX1
Maximum excitation limiter model |  |  | MAXEX2

## Turbine_Load_controller
7) Controlador de carga de la turbina
Denominación | IEEE standard | Modelo CIM | Modelo PSS/E
Turbine load controller model |  |  | LCFB1 *
* Este modelo se puede usar en combinación con los siguientes modelos de regulador de velocidad-turbina:

## Governors
8) Reguladores de velocidad-turbina (governors)
Denominación | IEEE standard | Modelo CIM | Modelo PSS/E | Revisión 2021
Brown-Boveri turbine-governor model |  |  | BBGOV1 | SI
Cross compound turbine-governor model |  |  | CRCMGV | NO
Woodward diesel governor model |  |  | DEGOV | NO
Woodward diesel governor model |  |  | DEGOV1 | NO
Woodward diesel governor model with speed deadband |  |  | DEGOV1DU | SI
Gas turbine-governor model |  |  | GAST | NO
Gas turbine-governor model |  |  | GAST2A | NO
Gas turbine model with speed deadband |  |  | GAST2ADU | SI
Gas turbine-governor with speed deadband |  |  | GASTDU | SI
Gas turbine-governor model |  |  | GASTWD | NO
Woodward gas turbine-governor model with speed deadband |  |  | GASTWDDU | SI
GE general purpose turbine-governor model |  | GovCT1 | GGOV1 | NO
GE general governor/turbine model with speed deadband |  |  | GGOV1DU | SI
Hydro turbine-governor model |  | GovHydro1 | HYGOV | NO
Hydro turbine-governor model with speed deadband |  |  | HYGOVDU | SI
Hydro turbine-governor model |  |  | HYGOV2 | NO
HYDro turbine-governor model with speed deadband |  |  | HYGOV2DU | SI
Hydro turbine-governor lumped parameter model |  |  | HYGOVM | NO
Fourth order lead-lag hydro-turbine |  |  | HYGOVRU | SI
Hydro turbine-governor traveling wave model |  |  | HYGOVT | NO
1981 IEEE type 1 turbine-governor model |  |  | IEEEG1 | NO
IEEE type 1 speed-governing model with speed deadband |  |  | IEEEG1SDU | SI
1981 IEEE type 2 turbine-governor model |  |  | IEEEG2 | NO
1981 IEEE type 3 turbine-governor model |  | GovHydro2 | IEEEG3 | NO
IEEE type 3 speed-governing model with speed deadband |  |  | IEEEG3DU | SI
1973 IEEE standard turbine-governor model |  |  | IEESGO | NO
IEEE standard model with speed deadband |  |  | IEESGODU | SI
IVO turbine-governor model |  |  | IVOGO | NO
Hydro turbine and governor model |  |  | PIDGOV | NO
Hydro turbine-governor model with speed deadband |  |  | PIDGOVDU | SI
Pratt & Whitney Turboden turbine-governor model |  |  | PWTBDU1 | NO
Torsional-elastic shaft model for 25 masses |  |  | SHAF25 | SI
Steam turbine-governor model |  | GovSteam0 | TGOV1 | NO
Steam turbine-governor model with speed deadband |  |  | TGOV1DU | SI
Steam turbine-governor model with fast valving |  |  | TGOV2 | NO
Modified IEEE type 1 turbine-governor model with fast valving |  |  | TGOV3 | NO
Modified IEEE type 1 speed-governing model with fast valving with speed deadband |  |  | TGOV3DU | SI
Modified IEEE type 1 speed governing model with PLU and EVA |  |  | TGOV4 | NO
Modified IEEE type 1 turbine-governor model with boiler controls |  |  | TGOV5 | NO
Czech hydro or steam turbine-governor model |  |  | TURCZT | SI
Tail water depression hydro governor model 1 |  |  | TWDM1T | NO
Tail water depression hydro governor model 2 |  |  | TWDM2T | NO
Combined cycle, single shaft turbine-governor model |  |  | URCSCT | NO
WECC gas turbine governor model |  |  | URGS3T | SI
Woodward electronic hydro governor model |  |  | WEHGOV | SI
Westinghouse digital governor for gas turbine |  |  | WESGOV | NO
Westinghouse digital governor for gas turbine model with speed deadband |  |  | WESGOVDU | SI
Woodward PID hydro governor model |  |  | WPIDHY | NO
Woodward PID hydro governor model with speed deadband |  |  | WPIDHYDU | SI
WECC double derivative hydro governor model |  |  | WSHYDD | SI
WECC GP hydro governor plus turbine model |  |  | WSHYGP | SI
WECC modified 1981 IEEE type 1 turbine-governor model | IEEE steam turbine/governor model | GovSteam1 | WSIEG1 | SI
Recomendado
Para la mayor parte de las turbinas de vapor se puede utilizar el modelo de librería de PSS/E denominado WSIEG1, que es el mismo que el IEEEG1, pero con banda muerta y otras no linealidades (que se pueden deshabilitar con la adecuada selección de parámetros), por lo que finalmente la única diferencia con el modelo IEEEG1 sería la banda muerta.
El modelo recomendado para turbinas de gas es el GGOV1 para la versión 32 de PSS/E y el UGGOV1 para versiones anteriores a la 32. Estos modelos también incorporan banda muerta.
Para generadores hidráulicos los modelos que se recomiendan, y que incluyen la posibilidad de parametrizar la banda muerta, son: WEHGOV, WSHYDD y WSHYGP.
Existen otros modelos de librería de PSS/E que también incorporan banda muerta y que fueron desarrollados para representar equipos específicos como: BBGOV1, TURCZT and URG3ST.
Note on E16: Sergio Martínez: Modelo genérico para cualquier turbina con un governor PID, recomendado para turbinas de gas y ciclos combinados. Los modelos UGGOV1 para versiones de PSSE anteriores a 32 también son válidos
Note on C56: Sergio Martinez: (con banda muerta opcional y ganancia no lineal añadida

## Generación _Eolica_FV
9) Generación eólica y fotovoltaica
Denominación | IEEE standard | Modelo CIM | Modelo PSS/E | Revisión 2021 | Comentarios
Generic Red Electrica model
|  |  | PPMREE |  | Ver Nota 1
Generic wind generator
User written generator model to represent photo-voltaic (PV) systems |  |  | PVGU1 | NO | Ver Nota 2
Renewable Energy Generator/Converter Model |  |  | REGCAU1 | NO | Ver Nota 2
Direct connected (Type 1) generator |  |  | WT1G1 | NO | Ver Nota 2
Induction generator with controlled external rotor resistor (Type 2) |  |  | WT2G1 | NO | Ver Nota 2
Doubly-fed induction generator (Type 3) |  |  | WT3G1 | NO | Ver Nota 2
Doubly-fed induction generator (Type 3) |  |  | WT3G2 | NO | Ver Nota 2
Wind generator model with power converter (Type 4) |  |  | WT4G1 | NO | Ver Nota 2
Wind generator model with power converter (Type 4), version 2 |  |  | WT4G2 | NO | Ver Nota 2
Generic wind electrical models
User written electrical control model for photo-voltaic (PV) systems |  |  | PVEU1 | NO | Ver Nota 2
Renewable Energy Electrical Model |  |  | REECAU1 | NO | Ver Nota 2
Renewable Energy Electrical Control model (for large scale PV) |  |  | REECBU1 | NO | Ver Nota 2
Electrical Control Model for Utility Scale Battery Energy Storage |  |  | REECCU1 | NO | Ver Nota 2
Rotor resistance control model for Type 2 wind generator |  |  | WT2E1 | NO | Ver Nota 2
Electrical control for Type 3 wind generator |  |  | WT3E1 | NO | Ver Nota 2
Electrical control models for Type 4 wind generator |  |  | WT4E1 | NO | Ver Nota 2
Electrical control for Type 4 wind generator, version 2 |  |  | WT4E2 | NO | Ver Nota 2
Generic wind mechanical models
User written model to represent the linearized model of PV panel’s output curve |  |  | PANELU1 | NO | Ver Nota 2
Wind turbine Mechanical system model |  |  | WTDTAU1 | NO | Ver Nota 2
Two mass turbine model for Type 1 and Type 2 wind generators |  |  | WT12T1 | NO | Ver Nota 2
Mechanical system model for Type 3 wind generator |  |  | WT3T1 | NO | Ver Nota 2
Generic wind pitch control models
User written model to represent the linearized model of PV panel’s solar irradiance profile. |  |  | IRRADU1 | NO | Ver Nota 2
Pitch control model for Type 3 wind generator |  |  | WT3P1 | NO | Ver Nota 2
Wind Turbine Pitch Control mode |  |  | WTPTAU1 | NO | Ver Nota 2
Generic aerodynamic wind models
Pseudo-governor model for Type 1 and Type 2 wind generators |  |  | WT12A1 | NO | Ver Nota 2
Wind Turbine Aerodynamic model |  |  | WTARAU1 | NO | Ver Nota 2
Generic wind auxiliary control models
Plant Controller model |  |  | REPCAU1 | NO | Ver Nota 2
Plant Controller model |  |  | REPCTAU1 | NO | Ver Nota 2
Auxiliary Control model for Type 4 machines |  |  | REAX4BU1 | NO | Ver Nota 2
Auxiliary Control model for Type 3 machines |  |  | REAX3BU1 | NO | Ver Nota 2
Nota 1: Pensado para representar modulos de parque eléctrico eólico full converter y fotovoltaicos que tengan obligación de cumplir los requisitos tecnicos de Reglamento Europeo, Orden TED 749/2020 o P.O. 12.2 SENP. Para eólicos doblemente alimentados puede no ajustarse al comportamiento dinámico dependiendo de control implementado por el fabricante. Solicitar documentación a través de infoestructural@ree.es.
Nota 2. Se puede admitir para generadores que no tengan que cumplir los requisitos tecnicos de Reglamento Europeo, Orden TED 749/2020 o P.O. 12.2 SENP

## SVC,FACTS,Shunts
10) SVC, FACTS, shunts
Denominación | IEEE standard | Modelo CIM | Modelo PSS/E
Static Condenser (modeled as FACTS device in power flow) |  |  | CSTCNT
SVC for switched shunt |  |  | CHSVCT
SVG for switched shunt |  |  | CSSCST
Switched shunt model |  |  | SWSHNT
WECC Generic STATCOM based SVC Model |  |  | SVSMO3U2
ABB SVC Model |  |  | ABBSVC1
SVC for switched shunt |  |  | CHSVCT
WECC Generic Continuous Control SVC model |  |  | SVSMO1U2
WECC Generic Discrete Control SVC Model |  |  | SVSMO2U2
Switched Shunt Auxiliary Control Model |  |  | SWSAXBU1

## protecciones
11) Protecciones de tensión y frecuencia (mínima y máxima)
Denominación | IEEE standard | Modelo CIM | Modelo PSS/E | Comentarios
Under/over frequency generator bus disconnection relay. |  |  | FRQDCA
Under/over frequency generator trip relay. |  |  | FRQTPA
Under/over voltage generator bus disconnection relay. |  |  | VGTDCA
Under/over voltage generator trip relay. |  |  | VTGTPA
Loss of excitation distance relay. |  |  | LOEXR1T
Modelo de relé (de tensión y frecuencia) desarrollado por REE |  |  | GPREE | Ver Nota 1
Volts per Hertz Model (to be applied only to synchronous machines) |  |  | VPERHZU1
Transformer saturation model. |  |  | SAT2T
Switched capacitor bank model. |  |  | SWCAPT
Nota 1: Se recomienda el uso de este relé para el modelado de las protecciónes de tensión y frecuencia. Solicitar documentación a través de infoestructural@ree.es

## REFERENCIAS
12) Referencias
[10] | PSSE 33.10 Model Library, April 2017, Siemens Energy Inc., Schenectady, NY, USA
[11] | PPMREE MODEL User Guide version 2, November 2018, Red Electrica
[12] | GPREE MODEL User Guide version 6, September 2021, Red Electrica